## ReadMe
Final Model
Project | 50 MW / 500 MWh behind-the-meter battery supplying a new 50 MW co-location load's Bring Your Own New Capacity (BYONC) under PJM IRAS (Dominion zone, Loudoun County), in service 1 June 2029.
Basis | Nominal US$ million, annual, end of period. Model years are PJM delivery years (1 June – 31 May): Year 0 = 2028/29 (construction), Years 1–15 = 2029/30 – 2043/44 (operation from 1 June 2029). Valued at the end of Year 0. Taxes use the same annual periods (simplification).
Signs | Inflows positive (+), outflows negative (-). DSCR = CFADS ÷ ¦debt service¦.
Colours | Orange fill = input; green fill = link to Inputs; yellow fill = key result; no fill = formula.
Sheets | Inputs → Events (PJM demand-response days, Dominion zone) → Technical → Costs → CashFlow → Results → Sensitivity → Customer.
Goal Seek | Goal Seek finds the fee that gives equity exactly a 12% return. Route: Data → What-If Analysis → Goal Seek; set Results!B23 to 0 by changing Inputs!C30. Re-run it after changing any input.
Sensitivity | 1. Fee by case: the minimum fee in 13 cases, e.g. low/high cost, capacity price, O&M, 5 h or 15 h, tax credit, interest rate, no recharge. 2. Case results: days covered, CAPEX and PJM charges in each case. 3. Cost limit: the highest CAPEX that still works if the customer will pay only $35, $30, $25 or the RBP cost.
Traceability | Base-case results: Results sheet. Sensitivity cases and thresholds: Sensitivity sheet. Customer-side comparisons (RBP, gas, rent): Customer sheet.

## Inputs
INPUTS AND SOURCES
| Parameter | Value | Unit | Evidence | Source
A. Timing and model basis
| Construction year (Year 0 = Jun 2028 – May 2029) | 2028 | year | Own design choice | Report Section 10 schedule.
| Contract term = operating life | 15 | years | Own design choice | NREL (2025) p.12.
| Inflation / cost escalation | 2.5% | %/year | Sourced | Lazard LCOE+ (Jul 2026).
| Dollar year of NREL cost inputs | 2024 | year | Sourced | NREL (2025).
| Dollar year of charging price | 2025 | year | Sourced | PJM Data Miner 2.
B. Customer load, PJM capacity requirement and battery performance
| New Large Load of the customer | 50 | MW | Sourced | PJM CIFP proposal (27 Jul 2026).
| Forecast Pool Requirement, 2029/30 | 0.9232 | ratio | Sourced | PJM 2029/30 BRA planning parameters (3 Sep 2026).
| Demand Resource accreditation, first delivery year 2029/30 | 90% | % | Sourced; applied beyond its basis | PJM ELCC class ratings, 2029/30 BRA.
| 10-hour storage accreditation, 2029/30 (rating comparison) | 76% | % | Sourced | PJM ELCC class ratings, 2029/30 BRA.
| Data center PUE (industry weighted average) | 1.54 | ratio | Sourced; applied beyond its basis | Uptime Institute survey (2025).
| Round-trip efficiency (AC, incl. auxiliary cooling) | 85% | % | Sourced | NREL (2025) p.12.
C. Capital cost and tax credit
| Energy-related installed cost (2024$) | 241 | $/kWh | Sourced | NREL (2025) p.6.
| Power-related installed cost (2024$) | 372 | $/kW | Sourced | NREL (2025) p.6.
| Investment tax credit rate | 30% | % | Sourced | IRS §48E; Notice 2026-15.
| Tax credit value when sold | 0.9 | $ per $1 credit | Sourced | Norton Rose Fulbright (Jan 2026).
| Depreciable basis reduction per $1 of credit | 0.5 | $ per $1 | Sourced | 26 U.S.C. §50(c)(3).
D. Operating cost
| Fixed O&M incl. augmentation | 4% | % of NREL capital cost per yr | Sourced; applied beyond its basis | NREL (2025) p.11.
| Insurance | 0.4% | % of CAPEX per year | Sourced; applied beyond its basis | PNNL (2024).
| Property tax | 0.84% | % of CAPEX per year | Sourced; applied beyond its basis | PNNL (2024).
| Charging energy price (2025$) | 47.53 | $/MWh | Sourced; held constant by judgment | PJM Data Miner 2 (DOM, 2025).
E. Revenue
| Availability fee per kW of load (Goal Seek) | 27.6535 | $/kW-month | Model output | Goal Seek output.
| Fee escalation | 0% | %/year | Own design choice | Contract design.
| Capacity price proxy (2029/30 RPM price cap) | 337.83 | $/MW-day UCAP | Sourced; held constant by judgment | PJM 2029/30 planning parameters (ER26-1556).
| Capacity price escalation | 0% | %/year nominal | Sourced; held constant by judgment | Held flat (judgment).
F. Customer value benchmark
| Northern Virginia colocation asking rate (low end) | 160 | $/kW-month | Sourced; point chosen from a range | CBRE H1 2026.
G. Tax
| Federal corporate income tax | 21% | % | Sourced | 26 U.S.C. §11(b).
| Virginia corporate income tax | 6% | % | Sourced | Va. Code Ann. §58.1-400.
| Loss carryforward limit | 80% | % of taxable income | Sourced | 26 U.S.C. §172(a).
| MACRS 5-year rate, tax year 1 | 20% | % of basis | Sourced | IRS Publication 946, Table A-1.
| MACRS 5-year rate, tax year 2 | 32% | % of basis | Sourced
| MACRS 5-year rate, tax year 3 | 19.2% | % of basis | Sourced
| MACRS 5-year rate, tax year 4 | 11.52% | % of basis | Sourced
| MACRS 5-year rate, tax year 5 | 11.52% | % of basis | Sourced
| MACRS 5-year rate, tax year 6 | 5.76% | % of basis | Sourced
H. Financing
| Base rate: 10-year U.S. Treasury yield (3 Sep 2026) | 4.77% | % | Sourced | Federal Reserve H.15 (4 Sep 2026).
| Term-debt margin (middle of fairway) | 1.75% | % | Sourced; point chosen from a range | Norton Rose Fulbright (Jan 2026).
| Battery storage premium | 0.25% | % | Sourced | Norton Rose Fulbright (Jan 2025).
| Uncontracted revenue share, first premium step | 10% | % of revenue | Sourced | Norton Rose Fulbright (Jan 2026).
| Premium at the first step | 0.25% | % | Sourced | Same source.
| Uncontracted revenue share, second premium step | 30% | % of revenue | Sourced | Norton Rose Fulbright (Jan 2026).
| Additional premium at the second step | 0.25% | % | Sourced | Same source.
| Debt tenor | 15 | years | Sourced | Lazard LCOE+ (Jul 2026).
| Minimum DSCR, contracted storage revenue | 1.2 | x | Sourced; point chosen from a range | Norton Rose Fulbright (Jan 2026).
| Minimum DSCR, merchant storage revenue | 2 | x | Sourced | Norton Rose Fulbright (Jan 2026).
| Target equity IRR (cost of equity) | 12% | % | Sourced | Lazard LCOE+ (Jul 2026).
I. Design duration, dispatch record and PJM performance charges
| Design duration (battery energy ÷ power) | 10 | h | Own design choice | Events sheet.
| Length of the event record | 9.72 | years | Sourced | PJM Emergency Procedures postings.
| Battery forced-outage rate in event hours | 8.94% | % | Sourced; applied beyond its basis | CPUC UCAP workshop (3 Nov 2025), slide 47.
| Net CONE, RTO, 2029/30 (installed capacity) | 261.79 | $/MW-day | Sourced | PJM 2029/30 planning parameters.
| Charge on non-PAI shortfalls, share of full rate | 50% | % | Sourced | FERC ER26-2319; PJM Manual 18.
J. PJM Demand Resource accreditation by delivery year (drives capacity revenue)
| Demand Resource ELCC class rating, 2029/30 | 90% | % | Sourced | Row 14.
| Demand Resource ELCC class rating, 2030/31 | 84% | % | Indicative (PJM preliminary, non-binding) | PJM preliminary ELCC ratings (31 Aug 2026).
| Demand Resource ELCC class rating, 2031/32 | 82% | % | Indicative (PJM preliminary, non-binding) | PJM preliminary ELCC ratings (31 Aug 2026).
| Demand Resource ELCC class rating, 2032/33 | 82% | % | Indicative (PJM preliminary, non-binding) | PJM preliminary ELCC ratings (31 Aug 2026).
| Demand Resource ELCC class rating, 2033/34 | 80% | % | Indicative (PJM preliminary, non-binding) | PJM preliminary ELCC ratings (31 Aug 2026).
| Demand Resource ELCC class rating, 2034/35 | 78% | % | Indicative (PJM preliminary, non-binding) | PJM preliminary ELCC ratings (31 Aug 2026).
| Demand Resource ELCC class rating, 2035/36 | 76% | % | Indicative (PJM preliminary, non-binding) | PJM preliminary ELCC ratings (31 Aug 2026).
| Demand Resource ELCC class rating, 2036/37 | 75% | % | Indicative (PJM preliminary, non-binding) | PJM preliminary ELCC ratings (31 Aug 2026).
| Demand Resource ELCC class rating, 2037/38 | 76% | % | Indicative (PJM preliminary, non-binding) | PJM preliminary ELCC ratings (31 Aug 2026).
| Demand Resource ELCC class rating, 2038/39 | 77% | % | Indicative (PJM preliminary, non-binding) | PJM preliminary ELCC ratings (31 Aug 2026).
| Demand Resource ELCC class rating, 2039/40 | 77% | % | Indicative (PJM preliminary, non-binding) | PJM preliminary ELCC ratings (31 Aug 2026).
| Demand Resource ELCC class rating, 2040/41 | 75% | % | Indicative (PJM preliminary, non-binding) | PJM preliminary ELCC ratings (31 Aug 2026).
| Demand Resource ELCC class rating, 2041/42 | 75% | % | Indicative (PJM preliminary, non-binding) | PJM preliminary ELCC ratings (31 Aug 2026).
| Demand Resource ELCC class rating, 2042/43 | 75% | % | Indicative (PJM preliminary, non-binding) | PJM preliminary ELCC ratings (31 Aug 2026).
| Demand Resource ELCC class rating, 2043/44 | 75% | % | Held at last published value (judgment) | Held at the 2042/43 value.
K. Sensitivity ranges and benchmarks
| NREL normalized installed-cost factor, construction year 2028 (mid projection) | 0.88 | × 2024 cost | Sourced | NREL (2025) Table 2.
| Capacity price floor, 2029/30 RPM auctions | 181.91 | $/MW-day UCAP | Sourced | PJM 2029/30 planning parameters.
| Simulated uncollared capacity price (2028/29 BRA) | 554.72 | $/MW-day UCAP | Sourced | PJM 2028/29 BRA report, p.20.
| RBP maximum MW-weighted average procurement cost | 555 | $/MW-day UCAP | Sourced | PJM RBP filing ER26-3380.
| Fixed O&M under NREL's literal 4-hour definition | 1.921% | % of NREL capital cost per yr | Sourced; derived | NREL (2025) p.11, Table 2.
| NREL cost factor, 2028 low projection | 0.69 | × 2024 cost | Sourced | NREL (2025) Table 2.
| NREL cost factor, 2028 high projection | 1.08 | × 2024 cost | Sourced | NREL (2025) Table 2.
| Investment tax credit without wage and apprenticeship rules | 6% | % | Sourced | IRS §48E.

## Events
PJM Demand-Response Dispatch Days in the Dominion Zone 1 Jan 2017 – 21 Sep 2026
Source: PJM Emergency Procedures postings (column I); PJM Winter Storm Elliott report (Jul 2023).
Date | Event (highest action) | Zones | Cuts due | Release | Hours | PAI (1 = yes) | Winter (Nov–Apr) | PJM postings | Follows a dispatch day (1/0) | Energy available at start (MWh) | Energy delivered (MWh) | Energy due but not delivered (MWh)
2019-10-02 | Pre-Emergency DR; PAI | AEP, BGE, DOM, PEPCO | 14:00 | 15:45 | 1.75 | 1 | 0 | EP 102663 | 0 | 500 | 87.5 | 0
2022-12-23 | Winter Storm Elliott: Pre-Emergency and Emergency DR, EEA2; PAI | PJM-wide | 18:00 | 22:15 | 4.25 | 1 | 1 | EP 103783–103790 | 0 | 500 | 212.5 | 0
2022-12-24 | Winter Storm Elliott: all DR, EEA2, Max Gen Emergency Action; PAI | PJM-wide | 6:00 | 20:30 | 14.5 | 1 | 1 | EP 103798–103808 | 1 | 500 | 500 | 225
2025-02-19 | Pre-Emergency DR | DOM Ashburn subzone | 16:20 | 22:15 | 5.9167 | 0 | 1 | EP 104514 | 0 | 500 | 295.8333 | 0
2025-06-23 | Pre-Emergency DR | Mid-Atlantic and DOM | 15:00 | 22:00 | 7 | 0 | 0 | EP 104654–104655 | 0 | 500 | 350 | 0
2025-06-24 | Pre-Emergency DR | PJM-wide (19 zones) | 15:00 | 22:00 | 7 | 0 | 0 | EP 104668–104669 | 1 | 500 | 350 | 0
2025-06-25 | Pre-Emergency DR | Mid-Atlantic, DOM, APS | 15:00 | 19:00 | 4 | 0 | 0 | EP 104686–104687 | 1 | 500 | 200 | 0
2025-07-28 | Pre-Emergency DR | BGE, DOM, PEPCO | 15:45 | 21:00 | 5.25 | 0 | 0 | EP 104744 | 0 | 500 | 262.5 | 0
2025-07-29 | Pre-Emergency DR | PJM-wide (19 zones) | 14:00 | 20:45 | 6.75 | 0 | 0 | EP 104748 | 1 | 500 | 337.5 | 0
2026-01-25 | Pre-Emergency DR (Winter Storm Fern) | BGE, DOM, PEPCO | 14:30 | 19:00 | 4.5 | 0 | 1 | EP 104978–104980 | 0 | 500 | 225 | 0
2026-05-18 | Pre-Emergency DR | BGE, DOM, PEPCO | 15:00 | 21:00 | 6 | 0 | 0 | EP 105094–105098 | 0 | 500 | 300 | 0
2026-05-19 | Pre-Emergency DR | BGE, DOM, PEPCO | 14:00 | 21:30 | 7.5 | 0 | 0 | EP 105113–105117 | 1 | 500 | 375 | 0
2026-07-02 | Pre-Emergency and Emergency DR, EEA2 | PJM-wide | 13:30 | 21:30 | 8 | 0 | 0 | EP 105291–105311 | 0 | 500 | 400 | 0
2026-07-03 | Pre-Emergency and Emergency DR, EEA2 | PJM-wide | 12:00 | 21:00 | 9 | 0 | 0 | EP 105334–105340 | 1 | 500 | 450 | 0
2026-09-01 | Pre-Emergency DR | AEP, BGE, COMED, DOM, PEPCO | 18:15 | 22:00 | 3.75 | 0 | 0 | EP 105472 | 0 | 500 | 187.5 | 0
2026-09-17 | Pre-Emergency and Emergency DR, EEA2 | 10 zones incl. DOM | 14:30 | 22:00 | 7.5 | 0 | 0 | EP 105532–105533 | 0 | 500 | 375 | 0

## Technical
Technical Model
1. Service requirement (BYONC)
New Large Load of the customer | 50 | MW
Forecast Pool Requirement | 0.9232 | ratio
BYONC requirement = load × FPR | 46.16 | MW UCAP
Battery power = new load (no export) | 50 | MW
Accreditation, first delivery year (Demand Resource) | 90% | %
Accredited capacity (UCAP), first delivery year | 45 | MW UCAP
Share of BYONC requirement covered | 97.49% | %
BYONC shortfall = requirement − accredited capacity | 1.16 | MW UCAP
Accredited capacity if rated as 10-hour storage | 38 | MW UCAP
Share of requirement covered at the storage rating | 82.32% | %
Shortfall at the storage rating | 8.16 | MW UCAP
Data center PUE (industry weighted average) | 1.54 | ratio
IT load protected by the service | 32.4675 | MW IT
2. Dispatch record (Events sheet)
Years in record | 9.72 | years
Demand-response days | 16 | days
Reduction hours in record | 102.6667 | hours
Average reduction hours per year | 10.5624 | hours/year
Winter days (November–April) | 4 | days
Longest event | 14.5 | hours
3. Sizing
Design duration in use | 10 | h
Demand-response days fully covered | 15 | days
Share of days fully covered | 93.75% | %
Battery power | 50 | MW
Usable energy = power × duration | 500 | MWh
Battery power (kW) | 50000 | kW
Usable energy (kWh) | 500000 | kWh
Customer load under contract (kW) | 50000 | kW
4. Event energy and PJM charges
Energy delivered per year | 504.9726 | MWh/year
Charging energy to restore it | 594.0854 | MWh/year
Round-trip losses | 89.1128 | MWh/year
Energy due but not delivered, PAI days | 23.1481 | MWh/year
Energy due but not delivered, other dispatch days | 0 | MWh/year
Expected outage shortfall, PAI days | 7.358 | MWh/year
Expected outage shortfall, other dispatch days | 37.7865 | MWh/year
Non-performance charge rate = Net CONE × 365 ÷ 30 | 3185.1117 | $/MWh
Expected PJM performance charges | 0.15734 | $M/year

## Costs
COSTS
Capital cost
(+) Energy component at the construction-year cost level (2024$) | 106.04 | $M
(+) Power component at the construction-year cost level (2024$) | 16.368 | $M
(=) NREL installed cost at the 2028 projection (2024$) | 122.408 | $M
Implied cost per usable kWh (2024$) | 244.816 | $/kWh
(×) Escalation factor, 2024 → construction year | 1.1038 | x
(=) Total CAPEX, construction-year dollars (Year 0) | 135.1155 | $M
Total CAPEX per kW | 2702.3106 | $/kW
Investment tax credit | 40.5347 | $M
ITC cash proceeds (Year 1) | 36.4812 | $M
Depreciable tax basis | 114.8482 | $M
Operating cost (Year 1 = first operating year, 2029/30)
(+) Fixed O&M incl. augmentation, Year 1 | 5.5397 | $M/year
(+) Property tax | 1.135 | $M/year
(+) Insurance | 0.54046 | $M/year
(+) Charging losses, Year 1 | 0.0046752 | $M/year
(+) Expected PJM performance charges | 0.15734 | $M/year
(=) Operating cost, Year 1 | 7.3772 | $M/year
Tax and financing rates
Combined income tax rate | 25.74% | %
Uncontracted (capacity) share of Year-1 revenue | 25.06% | %
Merchant-revenue spread premium | 0.25% | %
(=) All-in debt interest rate | 7.02% | %

## CashFlow
Cash Flow
Year index |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
PJM delivery year (June–May) |  | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39 | 2039/40 | 2040/41 | 2041/42 | 2042/43 | 2043/44
Operating flag | 1/0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Debt service flag | 1/0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Accredited capacity (UCAP) | MW | 0 | 45 | 42 | 41 | 41 | 40 | 39 | 38 | 37.5 | 38 | 38.5 | 38.5 | 37.5 | 37.5 | 37.5 | 37.5
Revenue
Customer load under contract | kW | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
(+) Availability fee revenue | $M | 0 | 16.5921 | 16.5921 | 16.5921 | 16.5921 | 16.5921 | 16.5921 | 16.5921 | 16.5921 | 16.5921 | 16.5921 | 16.5921 | 16.5921 | 16.5921 | 16.5921 | 16.5921
(+) PJM capacity revenue | $M | 0 | 5.5489 | 5.1789 | 5.0556 | 5.0556 | 4.9323 | 4.809 | 4.6857 | 4.624 | 4.6857 | 4.7474 | 4.7474 | 4.624 | 4.624 | 4.624 | 4.624
(=) Total revenue | $M | 0 | 22.1409 | 21.771 | 21.6477 | 21.6477 | 21.5244 | 21.4011 | 21.2778 | 21.2161 | 21.2778 | 21.3394 | 21.3394 | 21.2161 | 21.2161 | 21.2161 | 21.2161
Operating cost
(−) Fixed O&M incl. augmentation | $M | 0 | -5.5397 | -5.6782 | -5.8202 | -5.9657 | -6.1148 | -6.2677 | -6.4244 | -6.585 | -6.7496 | -6.9184 | -7.0913 | -7.2686 | -7.4503 | -7.6366 | -7.8275
(−) Property tax | $M | 0 | -1.135 | -1.135 | -1.135 | -1.135 | -1.135 | -1.135 | -1.135 | -1.135 | -1.135 | -1.135 | -1.135 | -1.135 | -1.135 | -1.135 | -1.135
(−) Insurance | $M | 0 | -0.54046 | -0.54046 | -0.54046 | -0.54046 | -0.54046 | -0.54046 | -0.54046 | -0.54046 | -0.54046 | -0.54046 | -0.54046 | -0.54046 | -0.54046 | -0.54046 | -0.54046
(−) Charging losses | $M | 0 | -0.0046752 | -0.0047921 | -0.0049119 | -0.0050347 | -0.0051606 | -0.0052896 | -0.0054218 | -0.0055574 | -0.0056963 | -0.0058387 | -0.0059847 | -0.0061343 | -0.0062877 | -0.0064449 | -0.006606
(−) Expected PJM performance charges | $M | 0 | -0.15734 | -0.15734 | -0.15734 | -0.15734 | -0.15734 | -0.15734 | -0.15734 | -0.15734 | -0.15734 | -0.15734 | -0.15734 | -0.15734 | -0.15734 | -0.15734 | -0.15734
(=) Total operating cost | $M | 0 | -7.3772 | -7.5158 | -7.6579 | -7.8035 | -7.9528 | -8.1058 | -8.2626 | -8.4233 | -8.5881 | -8.757 | -8.9301 | -9.1075 | -9.2894 | -9.4758 | -9.6669
(=) EBITDA | $M | 0 | 14.7637 | 14.2552 | 13.9898 | 13.8442 | 13.5716 | 13.2953 | 13.0152 | 12.7928 | 12.6897 | 12.5824 | 12.4093 | 12.1086 | 11.9267 | 11.7403 | 11.5492
Capital and incentives
(−) CAPEX | $M | -135.1155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(+) ITC cash proceeds | $M | 0 | 36.4812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unlevered tax (project view)
MACRS rate | % | 0% | 20% | 32% | 19.2% | 11.52% | 11.52% | 5.76% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
(−) Tax depreciation | $M | 0 | -22.9696 | -36.7514 | -22.0509 | -13.2305 | -13.2305 | -6.6153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(=) Taxable income before losses | $M | 0 | -8.2059 | -22.4962 | -8.061 | 0.61369 | 0.34111 | 6.6801 | 13.0152 | 12.7928 | 12.6897 | 12.5824 | 12.4093 | 12.1086 | 11.9267 | 11.7403 | 11.5492
Loss carryforward, opening | $M | 0 | 0 | 8.2059 | 30.7021 | 38.7631 | 38.2722 | 37.9993 | 32.6552 | 22.2431 | 12.0089 | 1.8571 | 0 | 0 | 0 | 0 | 0
Loss used | $M | 0 | 0 | 0 | 0 | 0.49095 | 0.27289 | 5.344 | 10.4121 | 10.2342 | 10.1517 | 1.8571 | 0 | 0 | 0 | 0 | 0
(=) Taxable income after losses | $M | 0 | 0 | 0 | 0 | 0.12274 | 0.068222 | 1.336 | 2.603 | 2.5586 | 2.5379 | 10.7253 | 12.4093 | 12.1086 | 11.9267 | 11.7403 | 11.5492
Loss carryforward, closing | $M | 0 | 8.2059 | 30.7021 | 38.7631 | 38.2722 | 37.9993 | 32.6552 | 22.2431 | 12.0089 | 1.8571 | 0 | 0 | 0 | 0 | 0 | 0
(−) Unlevered income tax | $M | 0 | 0 | 0 | 0 | -0.031593 | -0.01756 | -0.34389 | -0.67002 | -0.65857 | -0.65326 | -2.7607 | -3.1942 | -3.1168 | -3.0699 | -3.022 | -2.9728
(=) Project cash flow | $M | -135.1155 | 51.2449 | 14.2552 | 13.9898 | 13.8126 | 13.5541 | 12.9514 | 12.3452 | 12.1342 | 12.0364 | 9.8217 | 9.2152 | 8.9918 | 8.8568 | 8.7184 | 8.5765
Debt sizing
Contracted (fee) share of Year-1 revenue | % | 0 2028/29: 74.94%
Blended DSCR target | x | 0 2028/29: 1.4005
Sizing CFADS | $M |  | 14.7637 | 14.2552 | 13.9898 | 13.8126 | 13.5541 | 12.9514 | 12.3452 | 12.1342 | 12.0364 | 9.8217 | 9.2152 | 8.9918 | 8.8568 | 8.7184 | 8.5765
Minimum sizing CFADS | $M | 0 2028/29: 8.5765
Level annual debt service | $M | 0 2028/29: 6.1239
Debt raised | $M | 0 2028/29: 55.7055
Opening balance | $M | 0 | 55.7055 | 53.4921 | 51.1234 | 48.5884 | 45.8754 | 42.9719 | 39.8647 | 36.5393 | 32.9804 | 29.1718 | 25.0957 | 20.7336 | 16.0652 | 11.069 | 5.7222
(+) Debt draw | $M | 55.7055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(−) Interest | $M | 0 | -3.9105 | -3.7551 | -3.5889 | -3.4109 | -3.2205 | -3.0166 | -2.7985 | -2.5651 | -2.3152 | -2.0479 | -1.7617 | -1.4555 | -1.1278 | -0.77705 | -0.4017
(−) Principal | $M | 0 | -2.2134 | -2.3687 | -2.535 | -2.713 | -2.9034 | -3.1073 | -3.3254 | -3.5588 | -3.8087 | -4.076 | -4.3622 | -4.6684 | -4.9961 | -5.3468 | -5.7222
Closing balance | $M | 55.7055 | 53.4921 | 51.1234 | 48.5884 | 45.8754 | 42.9719 | 39.8647 | 36.5393 | 32.9804 | 29.1718 | 25.0957 | 20.7336 | 16.0652 | 11.069 | 5.7222 | 2.7534e-14
(−) Debt service | $M | 0 | -6.1239 | -6.1239 | -6.1239 | -6.1239 | -6.1239 | -6.1239 | -6.1239 | -6.1239 | -6.1239 | -6.1239 | -6.1239 | -6.1239 | -6.1239 | -6.1239 | -6.1239
Levered tax (equity view)
(=) Taxable income before losses | $M | 0 | -12.1164 | -26.2514 | -11.6499 | -2.7972 | -2.8793 | 3.6634 | 10.2167 | 10.2277 | 10.3744 | 10.5346 | 10.6476 | 10.6531 | 10.799 | 10.9633 | 11.1475
Loss carryforward, opening | $M | 0 | 0 | 12.1164 | 38.3678 | 50.0177 | 52.8149 | 55.6942 | 52.7635 | 44.5901 | 36.4079 | 28.1084 | 19.6807 | 11.1626 | 2.6401 | 0 | 0
Loss used | $M | 0 | 0 | 0 | 0 | 0 | 0 | 2.9307 | 8.1733 | 8.1822 | 8.2996 | 8.4277 | 8.5181 | 8.5225 | 2.6401 | 0 | 0
(=) Taxable income after losses | $M | 0 | 0 | 0 | 0 | 0 | 0 | 0.73269 | 2.0433 | 2.0455 | 2.0749 | 2.1069 | 2.1295 | 2.1306 | 8.1588 | 10.9633 | 11.1475
Loss carryforward, closing | $M | 0 | 12.1164 | 38.3678 | 50.0177 | 52.8149 | 55.6942 | 52.7635 | 44.5901 | 36.4079 | 28.1084 | 19.6807 | 11.1626 | 2.6401 | 0 | 0 | 0
(−) Levered income tax | $M | 0 | 0 | 0 | 0 | 0 | 0 | -0.18859 | -0.52595 | -0.52652 | -0.53408 | -0.54232 | -0.54814 | -0.54842 | -2.1001 | -2.8219 | -2.8694
Coverage and equity
(=) CFADS | $M | 0 | 14.7637 | 14.2552 | 13.9898 | 13.8442 | 13.5716 | 13.1067 | 12.4892 | 12.2663 | 12.1556 | 12.0401 | 11.8612 | 11.5602 | 9.8267 | 8.9184 | 8.6799
DSCR | x |  | 2.4108 | 2.3278 | 2.2845 | 2.2607 | 2.2162 | 2.1403 | 2.0394 | 2.003 | 1.9849 | 1.9661 | 1.9369 | 1.8877 | 1.6046 | 1.4563 | 1.4174
(=) Equity cash flow | $M | -79.41 | 45.121 | 8.1313 | 7.8659 | 7.7203 | 7.4477 | 6.9828 | 6.3653 | 6.1424 | 6.0317 | 5.9162 | 5.7373 | 5.4363 | 3.7028 | 2.7945 | 2.556
Cumulative equity cash flow | $M | -79.41 | -34.289 | -26.1577 | -18.2917 | -10.5714 | -3.1237 | 3.8591 | 10.2245 | 16.3668 | 22.3986 | 28.3148 | 34.0521 | 39.4884 | 43.1911 | 45.9856 | 48.5416
Cumulative project cash flow | $M | -135.1155 | -83.8706 | -69.6154 | -55.6255 | -41.8129 | -28.2589 | -15.3074 | -2.9623 | 9.1719 | 21.2083 | 31.0301 | 40.2453 | 49.2371 | 58.0939 | 66.8123 | 75.3887

## Results
RESULTS
Configuration and output
Battery power | 50 | MW
Usable energy | 500 | MWh
Accredited capacity (UCAP) | 45 | MW UCAP
Share of BYONC requirement covered | 97.49% | %
Costs, revenue and funding
Minimum battery service fee (solved) | 27.6535 | $/kW-month
Total CAPEX | 135.1155 | $M
ITC cash proceeds | 36.4812 | $M
Operating cost, Year 1 | 7.3772 | $M
Fee revenue, Year 1 | 16.5921 | $M
Capacity revenue, Year 1 | 5.5489 | $M
Total revenue, Year 1 | 22.1409 | $M
Capacity (uncontracted) share of Year-1 revenue | 25.06% | %
All-in debt interest rate | 7.02% | %
Minimum sizing CFADS | 8.5765 | $M
Debt raised | 55.7055 | $M
Gearing (debt ÷ CAPEX) | 41.23% | %
Equity contribution | 79.41 | $M
Financial performance
Equity NPV at target equity return | -3.6346e-06 | $M
Equity IRR | 12% | %
Project IRR (unlevered, after tax) | 8.676% | %
Minimum DSCR | 1.4174 | x
Blended DSCR target | 1.4005 | x
Customer value
IT capacity of the load | 32.4675 | MW IT
Colocation rent of that IT capacity | 62.3377 | $M/year
Year-1 fee as share of that rent | 26.62% | %
Design basis and PJM performance risk
Design duration | 10 | h
Dominion demand-response days fully covered | 15 | days
Expected PJM performance charges | 0.15734 | $M/year
Model checks
Equity NPV at 12% (0 once Goal Seek is current) | -3.6346e-06 | OK
Debt balance after Year 15 (should be 0) | 2.7534e-14 | OK
Minimum DSCR minus lender target (should be 0 or more) | 0.016884 | OK
Additional metrics
Average DSCR | 1.9958 | x
Equity payback, operating year | 6 | year
Equity payback, delivery year | 2034/35
Project payback, operating year | 8 | year
Project payback, delivery year | 2036/37
First year with income tax, operating year | 6 | year
First year with income tax, delivery year | 2034/35
Project NPV at the debt rate | 10.173 | $M
Fee per accredited MW-day | 1010.172 | $/MW-day
EBITDA margin, Year 1 | 66.68% | %
EBITDA margin, Year 15 | 54.44% | %
DSCR, Year 1 | 2.4108 | x
DSCR, Year 15 | 1.4174 | x
Level annual debt service | 6.1239 | $M/year
15-year totals (Years 1–15)
Fee revenue | 248.8811 | $M
Capacity revenue | 72.5667 | $M
Total revenue | 321.4479 | $M
Operating cost | 126.9136 | $M
Income tax | 11.2054 | $M
Debt service | 91.8584 | $M
Cash to equity from operations (excl. tax credit) | 91.4704 | $M
Tax credit proceeds | 36.4812 | $M
Share of revenue: operating cost | 39.48% | %
Share of revenue: debt service | 28.58% | %
Share of revenue: income tax | 3.486% | %
Share of revenue: cash to equity | 28.46% | %

## Sensitivity
Sensitivity
Active case
Case number (blank = base case)
Trial fee, $/kW-month (blank = solved fee on Inputs)
NREL cost factor in use | 0.88
Capacity price in use ($/MW-day) | 337.83
Fixed O&M rate in use (% of cost) | 4%
Design duration in use (h) | 10
Fee in use ($/kW-month) | 27.6535
Tax-credit rate in use | 30%
Treasury base rate in use | 4.77%
Overnight recharge between consecutive dispatch days (1 = yes) | 1
NREL cost factor override (blank; used only by the threshold Data Table)
Cases
Case | NREL cost factor | Capacity price ($/MW-day) | Fixed O&M (% of cost) | Duration (h) | Tax-credit rate | Treasury base rate | Overnight recharge (1/0)
1 Base case | 0.88 | 337.83 | 4% | 10 | 30% | 4.77% | 1
2 Installed cost: NREL 2028 low | 0.69 | 337.83 | 4% | 10 | 30% | 4.77% | 1
3 Installed cost: NREL 2028 high | 1.08 | 337.83 | 4% | 10 | 30% | 4.77% | 1
4 Capacity price: 2029/30 floor | 0.88 | 181.91 | 4% | 10 | 30% | 4.77% | 1
5 Capacity price: uncollared | 0.88 | 554.72 | 4% | 10 | 30% | 4.77% | 1
6 Fixed O&M: NREL literal | 0.88 | 337.83 | 1.921% | 10 | 30% | 4.77% | 1
7 Duration 5 h | 0.88 | 337.83 | 4% | 5 | 30% | 4.77% | 1
8 Duration 15 h | 0.88 | 337.83 | 4% | 15 | 30% | 4.77% | 1
9 Tax credit 6% | 0.88 | 337.83 | 4% | 10 | 6% | 4.77% | 1
10 Tax credit 0% | 0.88 | 337.83 | 4% | 10 | 0% | 4.77% | 1
11 Treasury base rate +1 point | 0.88 | 337.83 | 4% | 10 | 30% | 5.77% | 1
12 Treasury base rate −1 point | 0.88 | 337.83 | 4% | 10 | 30% | 3.77% | 1
13 No overnight recharge | 0.88 | 337.83 | 4% | 10 | 30% | 4.77% | 0
Minimum fee and outputs by case | [7 empty] | Data Table 1: equity NPV at 12% ($M) by case (rows) and trial fee (columns) | [57 empty] | Data Table 3: case outputs
Case | Minimum fee ($/kW-month) | Change vs base | Fee share of rent | Days covered (of 16) | CAPEX ($M) | PJM charges ($M/yr) | Helper | -3.6346e-06 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 |  |  | 15 | 135.1155 | 0.15734 | 23.1481
1 Base case | 27.6534 | 0 | 26.62% | 15 | 135.1155 | 0.15734 | 23 | 1 | -106.3229 | -101.5385 | -96.7448 | -91.936 | -87.1423 | -82.347 | -77.5331 | -72.7026 | -67.8572 | -62.9986 | -58.128 | -53.2465 | -48.3552 | -43.455 | -38.5465 | -33.6306 | -30.3955 | -25.7757 | -21.0075 | -16.318 | -11.8243 | -7.3571 | -2.9028 | 1.54 | 5.9609 | 10.3777 | 14.7742 | 19.1638 | 23.5496 | 27.9109 | 32.269 | 36.6211 | 40.9454 | 45.2718 | 49.6003 | 53.928 | 58.2284 | 62.5305 | 66.8342 | 71.1396 | 75.4461 | 79.7233 | 84.002 | 88.2819 | 92.563 | 96.8454 | 101.1289 | 105.4042 | 109.6601 | 113.917 | 118.1748 | 122.4336 | 126.6933 | 130.9496 | 135.1802 | 139.4115 |  | 1 | 15 | 135.1155 | 0.15734 | 23.1481
2 Installed cost: NREL 2028 low | 20.2218 | -7.4315 | 19.46% | 15 | 105.9429 | 0.15734 | 16 | 2 | -70.0028 | -65.2604 | -60.4914 | -55.6991 | -50.8865 | -46.0559 | -41.2093 | -36.3486 | -31.4752 | -26.5904 | -23.5136 | -18.8163 | -14.1638 | -9.7428 | -5.3423 | -0.96679 | 3.3913 | 8.434 | 12.8026 | 17.1658 | 21.5086 | 25.8441 | 30.1542 | 34.464 | 38.7771 | 43.067 | 47.3538 | 51.6434 | 55.9354 | 60.2015 | 64.4669 | 68.7345 | 73.0041 | 77.2756 | 81.5267 | 85.7718 | 90.0185 | 94.2667 | 98.5151 | 102.7376 | 106.9423 | 111.134 | 115.3269 | 119.5209 | 123.7073 | 127.8859 | 132.0654 | 136.246 | 140.4275 | 144.6099 | 148.7932 | 152.9773 | 157.1621 | 161.3478 | 165.5341 | 169.7149 |  | 2 | 15 | 105.9429 | 0.15734 | 23.1481
3 Installed cost: NREL 2028 high | 35.6158 | 7.9624 | 34.28% | 15 | 165.8236 | 0.15734 | 31 | 3 | -144.6608 | -139.9169 | -135.1361 | -130.3246 | -125.498 | -120.6651 | -115.8215 | -110.9701 | -106.1541 | -101.323 | -96.4782 | -91.6208 | -86.7521 | -81.8731 | -76.9847 | -72.0877 | -67.1828 | -61.7137 | -56.7359 | -51.7516 | -46.7611 | -41.765 | -37.1727 | -35.0761 | -30.2954 | -25.5112 | -20.7239 | -16.2006 | -11.6995 | -7.2157 | -2.7448 | 1.7124 | 6.162 | 10.5913 | 15.0228 | 19.4326 | 23.835 | 28.2392 | 32.6255 | 36.9998 | 41.3709 | 45.7366 | 50.0811 | 54.4178 | 58.7558 | 63.0952 | 67.4358 | 71.7537 | 76.065 | 80.3775 | 84.6911 | 89.0057 | 93.3212 | 97.6238 | 101.9103 | 106.1978 |  | 3 | 15 | 165.8236 | 0.15734 | 23.1481
4 Capacity price: 2029/30 floor | 31.1712 | 3.5178 | 30% | 15 | 135.1155 | 0.15734 | 27 | 4 | -124.9459 | -120.1666 | -115.3378 | -110.4685 | -105.5709 | -100.6643 | -95.7505 | -90.8306 | -85.8947 | -80.9435 | -75.9788 | -71.0023 | -66.0155 | -61.0195 | -56.0153 | -51.0037 | -45.9857 | -40.9617 | -35.9323 | -30.8981 | -28.6931 | -23.8873 | -19.0786 | -14.3145 | -9.7794 | -5.2674 | -0.76673 | 3.7129 | 8.1803 | 12.6314 | 17.0752 | 21.4968 | 25.92 | 30.3222 | 34.715 | 39.0996 | 43.4689 | 47.8219 | 52.176 | 56.5311 | 62.3866 | 66.7598 | 71.134 | 75.5091 | 79.885 | 84.2454 | 88.5918 | 92.939 | 97.2868 | 101.6353 | 105.9845 | 110.3342 | 114.6624 | 118.9834 | 123.305 | 127.6271 |  | 4 | 15 | 135.1155 | 0.15734 | 23.1481
5 Capacity price: uncollared | 22.874 | -4.7794 | 22.02% | 15 | 135.1155 | 0.15734 | 18 | 5 | -81.3072 | -76.5847 | -71.8425 | -67.0824 | -62.3059 | -57.5144 | -52.7091 | -47.8913 | -43.0617 | -38.2215 | -33.374 | -30.6177 | -26.0027 | -21.3277 | -16.8857 | -12.5047 | -8.1365 | -3.7888 | 0.5463 | 4.8707 | 9.1813 | 13.481 | 17.7808 | 22.0544 | 26.3253 | 30.5915 | 34.8314 | 39.0746 | 43.3209 | 47.5629 | 51.7829 | 57.2984 | 61.5676 | 65.8394 | 70.0938 | 74.3389 | 78.5863 | 82.8358 | 87.0874 | 91.3409 | 95.5911 | 99.8183 | 104.0471 | 108.2777 | 112.5099 | 116.7437 | 120.9726 | 125.1781 | 129.3568 | 133.5338 | 137.712 | 141.8916 | 146.0723 | 150.2503 | 154.4156 | 158.5819 |  | 5 | 15 | 135.1155 | 0.15734 | 23.1481
6 Fixed O&M: NREL literal | 22.0741 | -5.5793 | 21.25% | 15 | 135.1155 | 0.15734 | 18 | 6 | -79.3854 | -74.5938 | -69.78 | -64.9467 | -60.0965 | -55.2312 | -50.3526 | -45.4622 | -40.5612 | -35.6506 | -31.414 | -28.4284 | -23.7078 | -18.9822 | -14.452 | -10.0072 | -5.5795 | -0.3295 | 4.1199 | 8.5411 | 12.9649 | 17.3657 | 21.7623 | 26.1565 | 30.5248 | 34.893 | 39.2544 | 43.5886 | 47.922 | 52.2574 | 56.5947 | 60.9083 | 65.2172 | 69.5277 | 73.8396 | 78.1528 | 82.4493 | 86.7343 | 91.0204 | 95.3077 | 99.5961 | 103.8855 | 108.1759 | 112.445 | 116.7077 | 120.9711 | 125.2354 | 129.5005 | 133.7663 | 138.0194 | 142.2559 | 146.4932 | 150.7084 | 154.9161 | 159.1244 | 163.3333 |  | 6 | 15 | 135.1155 | 0.15734 | 23.1481
7 Duration 5 h | 12.9058 | -14.7475 | 12.42% | 5 | 76.5914 | 0.38051 | 8 | 7 | -35.4488 | -30.6615 | -25.8515 | -21.0218 | -17.3681 | -12.7192 | -8.279 | -3.923 | 0.4078 | 4.7177 | 9.011 | 13.2798 | 17.5348 | 21.7696 | 26.0093 | 30.2229 | 34.4415 | 39.4488 | 43.6885 | 47.9323 | 52.1798 | 56.4065 | 60.6306 | 64.8578 | 69.074 | 73.2505 | 77.4231 | 81.5982 | 85.7668 | 89.9284 | 94.092 | 98.2576 | 102.425 | 106.594 | 110.7647 | 114.9368 | 119.1021 | 123.2635 | 127.4262 | 131.5901 | 135.7552 | 139.9215 | 144.0887 | 148.257 | 152.4263 | 156.5965 | 160.7619 | 164.9255 | 169.0899 | 173.2551 | 177.421 | 181.5876 | 185.7549 | 189.9229 | 194.0915 | 198.2606 |  | 7 | 5 | 76.5914 | 0.38051 | 151.3203
8 Duration 15 h | 42.7131 | 15.0597 | 41.11% | 16 | 193.6397 | 0.090205 | 38 | 8 | -178.8492 | -174.153 | -169.4154 | -164.642 | -159.837 | -155.0042 | -150.1543 | -145.297 | -140.4344 | -135.5626 | -130.6859 | -125.8419 | -120.993 | -116.1326 | -111.2617 | -106.3812 | -101.4919 | -96.2131 | -91.2503 | -86.2801 | -81.3031 | -76.3198 | -71.3306 | -66.3359 | -61.3362 | -56.3317 | -51.3228 | -46.3097 | -42.6995 | -40.2596 | -35.4683 | -30.6745 | -25.8783 | -21.1921 | -16.6716 | -12.1646 | -7.6707 | -3.1847 | 1.2814 | 5.7493 | 10.1952 | 14.6341 | 19.0745 | 23.4941 | 27.9045 | 32.3164 | 36.7296 | 41.1108 | 45.4931 | 49.8721 | 54.2451 | 58.6055 | 62.9488 | 67.293 | 71.6383 | 75.9845 |  | 8 | 16 | 193.6397 | 0.090205 | 0
9 Tax credit 6% | 33.3 | 5.6466 | 32.05% | 15 | 135.1155 | 0.15734 | 29 | 9 | -132.3809 | -127.5965 | -122.8028 | -117.994 | -113.2003 | -108.405 | -103.5911 | -98.7606 | -93.9152 | -89.0566 | -84.186 | -79.3045 | -74.4132 | -69.513 | -64.6045 | -59.6886 | -54.7658 | -49.0793 | -45.7159 | -42.2685 | -37.4917 | -32.7109 | -28.1029 | -23.6004 | -19.122 | -14.6521 | -10.1993 | -5.7541 | -1.3284 | 3.0999 | 7.5008 | 11.9006 | 16.3026 | 20.674 | 25.0463 | 29.41 | 33.7632 | 38.0971 | 42.4326 | 46.7697 | 51.1082 | 55.4252 | 59.7348 | 64.0456 | 68.3577 | 72.671 | 76.9854 | 81.2746 | 85.5602 | 89.8468 | 94.1343 | 98.4228 | 102.7121 | 107.0023 | 111.2898 | 115.5519 |  | 9 | 15 | 135.1155 | 0.15734 | 23.1481
10 Tax credit 0% | 34.7095 | 7.0562 | 33.41% | 15 | 135.1155 | 0.15734 | 30 | 10 | -138.8954 | -134.111 | -129.3173 | -124.5085 | -119.7148 | -114.9195 | -110.1056 | -105.2751 | -100.4297 | -95.5711 | -90.7005 | -85.819 | -80.9277 | -76.0275 | -71.119 | -66.2031 | -61.2803 | -55.5938 | -50.599 | -48.7769 | -44.0001 | -39.2193 | -34.435 | -29.9167 | -25.4193 | -20.9376 | -16.4713 | -12.0156 | -7.572 | -3.1438 | 1.287 | 5.6887 | 10.0906 | 14.4946 | 18.87 | 23.2442 | 27.6113 | 31.9722 | 36.3077 | 40.6447 | 44.9833 | 49.3232 | 53.6524 | 57.9633 | 62.2754 | 66.5887 | 70.903 | 75.2185 | 79.5255 | 83.8121 | 88.0996 | 92.3881 | 96.6774 | 100.9676 | 105.2585 | 109.5503 |  | 10 | 15 | 135.1155 | 0.15734 | 23.1481
11 Treasury base rate +1 point | 28.39 | 0.73664 | 27.33% | 15 | 135.1155 | 0.15734 | 24 | 11 | -105.6886 | -101.0831 | -96.4746 | -91.857 | -87.2542 | -82.6507 | -78.0331 | -73.403 | -68.7616 | -64.1101 | -59.4496 | -54.7809 | -50.1046 | -45.4216 | -40.7324 | -36.0376 | -32.6153 | -28.0593 | -23.4717 | -18.8806 | -14.5331 | -10.2271 | -5.9315 | -1.6636 | 2.602 | 6.8433 | 11.0871 | 15.302 | 19.5183 | 23.7259 | 27.9138 | 32.0984 | 36.2771 | 40.4282 | 44.581 | 48.7353 | 52.8912 | 57.0219 | 61.15 | 65.2794 | 69.4101 | 73.5419 | 77.6587 | 81.763 | 85.8684 | 89.9747 | 94.082 | 98.1902 | 102.2992 | 106.3947 | 110.477 | 114.56 | 118.6437 | 122.7282 | 126.8133 | 130.8969 |  | 11 | 15 | 135.1155 | 0.15734 | 23.1481
12 Treasury base rate −1 point | 26.9063 | -0.74708 | 25.9% | 15 | 135.1155 | 0.15734 | 22 | 12 | -107.0222 | -102.0402 | -97.0425 | -92.0231 | -87.0192 | -82.0125 | -76.9823 | -71.9311 | -66.8611 | -61.7743 | -56.6722 | -51.5565 | -46.4282 | -41.2887 | -36.1387 | -30.9798 | -27.9505 | -23.259 | -18.2918 | -13.5252 | -8.8544 | -4.1974 | 0.43404 | 5.0554 | 9.6618 | 14.256 | 18.8354 | 23.4155 | 27.9667 | 32.5148 | 37.0559 | 41.5701 | 46.0871 | 50.6066 | 55.1173 | 59.6082 | 64.1014 | 68.5966 | 73.0938 | 77.5757 | 82.044 | 86.5141 | 90.9858 | 95.4591 | 99.9338 | 104.4042 | 108.8505 | 113.2981 | 117.747 | 122.197 | 126.6482 | 131.0892 | 135.5102 | 139.9194 | 144.3098 | 148.7011 |  | 12 | 15 | 135.1155 | 0.15734 | 23.1481
13 No overnight recharge | 28.0067 | 0.3533 | 26.96% | 10 | 135.1155 | 0.37368 | 24 | 13 | -108.0549 | -103.2684 | -98.4719 | -93.6632 | -88.8543 | -84.0627 | -79.2521 | -74.4248 | -69.5824 | -64.7265 | -59.8585 | -54.9794 | -50.0904 | -45.1922 | -40.2858 | -35.3717 | -31.0386 | -27.4644 | -22.6975 | -17.9261 | -13.413 | -8.9361 | -4.4712 | -0.029555 | 4.4022 | 8.818 | 13.2257 | 17.6143 | 22.0057 | 26.3719 | 30.7335 | 35.0869 | 39.4201 | 43.7457 | 48.0733 | 52.403 | 56.7117 | 61.0131 | 65.3161 | 69.6208 | 73.927 | 78.2147 | 82.4927 | 86.772 | 91.0526 | 95.3344 | 99.6173 | 103.9014 | 108.1585 | 112.4149 | 116.6722 | 120.9306 | 125.1898 | 129.4486 | 133.6871 | 137.918 |  | 13 | 10 | 135.1155 | 0.37368 | 150.463
Tornado summary
Input and range | Fee, low input | Fee, high input | Difference
Installed cost: NREL 2028 low / high (0.69 / 1.08) | 20.2218 | 35.6158 | 15.394
Capacity price: $181.91 floor / $554.72 uncollared | 31.1712 | 22.874 | 8.2972
Fixed O&M: NREL literal 1.92% / base 4% | 22.0741 | 27.6534 | 5.5793
Thresholds
Minimum fee for a 12% equity return (base case) | 27.6534
Fee change per 10% of base CAPEX | 3.4735
Base CAPEX ($M) | 135.1155
Maximum CAPEX for a customer fee ceiling | [7 empty] | Data Table 2: equity NPV at 12% ($M) by fee ceiling (rows) and NREL cost factor (columns)
Customer's maximum fee ($/kW-month) | Basis | Maximum NREL cost factor | CAPEX change vs base | Maximum CAPEX ($M) |  |  | Helper | -3.6346e-06 | 0.2 | 0.21 | 0.22 | 0.23 | 0.24 | 0.25 | 0.26 | 0.27 | 0.28 | 0.29 | 0.3 | 0.31 | 0.32 | 0.33 | 0.34 | 0.35 | 0.36 | 0.37 | 0.38 | 0.39 | 0.4 | 0.41 | 0.42 | 0.43 | 0.44 | 0.45 | 0.46 | 0.47 | 0.48 | 0.49 | 0.5 | 0.51 | 0.52 | 0.53 | 0.54 | 0.55 | 0.56 | 0.57 | 0.58 | 0.59 | 0.6 | 0.61 | 0.62 | 0.63 | 0.64 | 0.65 | 0.66 | 0.67 | 0.68 | 0.69 | 0.7 | 0.71 | 0.72 | 0.73 | 0.74 | 0.75 | 0.76 | 0.77 | 0.78 | 0.79 | 0.8 | 0.81 | 0.82 | 0.83 | 0.84 | 0.85 | 0.86 | 0.87 | 0.88 | 0.89 | 0.9 | 0.91 | 0.92 | 0.93 | 0.94 | 0.95 | 0.96 | 0.97 | 0.98 | 0.99 | 1 | 1.01 | 1.02 | 1.03 | 1.04 | 1.05 | 1.06 | 1.07 | 1.08 | 1.09 | 1.1 | 1.11 | 1.12 | 1.13 | 1.14 | 1.15 | 1.16 | 1.17 | 1.18 | 1.19 | 1.2 | 1.21 | 1.22 | 1.23 | 1.24 | 1.25 | 1.26 | 1.27 | 1.28 | 1.29 | 1.3
35 | Round-number test | 1.0645 | 20.97% | 163.4474 |  |  | 87 | 35 | 142.354 | 140.7958 | 139.2376 | 137.6794 | 136.1212 | 134.563 | 133.0049 | 131.4467 | 129.8885 | 128.3303 | 126.7721 | 125.2139 | 123.6558 | 122.0976 | 120.5394 | 118.9812 | 117.423 | 115.8648 | 114.3036 | 112.7351 | 111.1667 | 109.5983 | 108.0299 | 106.4615 | 104.8931 | 103.3243 | 101.7421 | 100.1598 | 98.5775 | 96.9952 | 95.413 | 93.8307 | 92.2484 | 90.6661 | 89.0724 | 87.4748 | 85.8773 | 84.2798 | 82.6684 | 81.0375 | 79.3903 | 77.743 | 76.0957 | 74.4484 | 72.8011 | 71.1406 | 69.4722 | 67.8038 | 66.1353 | 64.4669 | 62.7985 | 61.1301 | 59.4617 | 57.7748 | 56.0868 | 54.3989 | 52.711 | 51.0231 | 49.3351 | 47.6472 | 45.9468 | 44.2408 | 42.5348 | 40.8289 | 39.1229 | 37.417 | 35.711 | 33.9917 | 32.269 | 30.546 | 28.8174 | 27.0888 | 25.3603 | 23.6247 | 21.88 | 20.1352 | 18.3904 | 16.6457 | 14.9009 | 13.1483 | 11.3885 | 9.6288 | 7.8691 | 6.1093 | 4.3496 | 2.576 | 0.80242 | -0.97119 | -2.7448 | -4.5184 | -6.3021 | -8.0885 | -9.875 | -11.6615 | -13.4479 | -15.2448 | -17.0432 | -18.8416 | -20.6399 | -22.465 | -24.3667 | -26.2683 | -28.1699 | -30.0716 | -31.9732 | -33.8748 | -35.7764 | -37.6781 | -39.5797 | -41.4813 | -42.9714
30 | Round-number test | 0.93892 | 6.696% | 144.1622 |  |  | 74 | 30 | 121.5783 | 120.0229 | 118.4676 | 116.9122 | 115.3568 | 113.8014 | 112.246 | 110.6907 | 109.1353 | 107.5799 | 106.0245 | 104.4691 | 102.9138 | 101.3584 | 99.7989 | 98.2333 | 96.6677 | 95.1021 | 93.5364 | 91.9708 | 90.4052 | 88.8265 | 87.247 | 85.6675 | 84.088 | 82.5085 | 80.929 | 79.3495 | 77.7607 | 76.166 | 74.5712 | 72.9764 | 71.3647 | 69.726 | 68.0813 | 66.4367 | 64.792 | 63.1474 | 61.4874 | 59.8216 | 58.1558 | 56.49 | 54.8242 | 53.1584 | 51.4926 | 49.8083 | 48.123 | 46.4377 | 44.7523 | 43.067 | 41.3816 | 39.6863 | 37.9829 | 36.2795 | 34.576 | 32.8726 | 31.1692 | 29.4578 | 27.7377 | 26.0173 | 24.2914 | 22.5653 | 20.8392 | 19.0992 | 17.3569 | 15.6145 | 13.8722 | 12.1299 | 10.3777 | 8.6204 | 6.8631 | 5.1058 | 3.3485 | 1.58 | -0.19117 | -1.9624 | -3.7336 | -5.5077 | -7.2918 | -9.0759 | -10.86 | -12.6441 | -14.439 | -16.2351 | -18.0311 | -19.8272 | -21.7122 | -23.6117 | -25.5112 | -27.4107 | -29.3103 | -31.2098 | -33.1093 | -35.0088 | -36.9083 | -38.2751 | -39.1239 | -39.9726 | -41.1353 | -43.0757 | -45.0161 | -46.9564 | -48.8968 | -50.8372 | -52.7776 | -54.718 | -56.6584 | -58.5988 | -60.5392 | -62.4796 | -64.42
25 | Round-number test | 0.8134 | -7.568% | 124.8894 |  |  | 62 | 25 | 100.8473 | 99.2954 | 97.7435 | 96.1917 | 94.6398 | 93.0879 | 91.536 | 89.9841 | 88.4322 | 86.8803 | 85.3233 | 83.7612 | 82.199 | 80.6369 | 79.0747 | 77.5126 | 75.9383 | 74.3623 | 72.7862 | 71.2102 | 69.6341 | 68.0581 | 66.4748 | 64.8835 | 63.2921 | 61.7008 | 60.0839 | 58.4425 | 56.8012 | 55.1599 | 53.5186 | 51.8594 | 50.1969 | 48.5343 | 46.8718 | 45.2093 | 43.5467 | 41.8653 | 40.1832 | 38.5011 | 36.819 | 35.1368 | 33.447 | 31.7467 | 30.0465 | 28.3462 | 26.646 | 24.9429 | 23.2259 | 21.5086 | 19.7859 | 18.063 | 16.335 | 14.5958 | 12.8565 | 11.1173 | 9.378 | 7.6266 | 5.8723 | 4.118 | 2.3637 | 0.60081 | -1.1674 | -2.9357 | -4.7039 | -6.4808 | -8.262 | -10.0431 | -11.8243 | -13.6169 | -15.4101 | -17.2032 | -19.0456 | -20.9425 | -22.8394 | -24.7363 | -26.6332 | -28.53 | -30.4269 | -32.3238 | -33.5734 | -34.4399 | -35.3065 | -37.0759 | -39.0129 | -40.95 | -42.887 | -44.8241 | -46.7611 | -48.6982 | -50.6352 | -52.5723 | -54.5093 | -56.4464 | -58.3834 | -60.3205 | -62.2575 | -64.1946 | -66.1316 | -68.0687 | -70.0057 | -71.9428 | -73.8798 | -75.8169 | -77.754 | -79.691 | -81.6281 | -83.5651 | -85.5022 | -87.4392 | -89.3763
15.5848 | RBP route, auction price $0 | 0.57451 | -34.72% | 88.2099 |  |  | 38 | 15.5848 | 61.2964 | 59.7607 | 58.2206 | 56.6746 | 55.1287 | 53.5828 | 52.0314 | 50.4715 | 48.9116 | 47.3517 | 45.7919 | 44.2201 | 42.6448 | 41.0696 | 39.4624 | 37.837 | 36.2116 | 34.5749 | 32.9282 | 31.2815 | 29.6348 | 27.981 | 26.3147 | 24.6483 | 22.9819 | 21.3074 | 19.6228 | 17.9382 | 16.2536 | 14.5568 | 12.8546 | 11.1473 | 9.4353 | 7.7115 | 5.9877 | 4.2624 | 2.5235 | 0.78456 | -0.95662 | -2.7095 | -4.4624 | -6.2205 | -7.9864 | -9.7523 | -11.5277 | -13.3057 | -15.1212 | -17.0033 | -18.8855 | -20.7676 | -22.6497 | -24.4381 | -25.4046 | -26.5021 | -28.4196 | -30.3378 | -32.256 | -34.1743 | -36.0925 | -38.0107 | -39.9289 | -41.8472 | -43.7654 | -45.6836 | -47.6018 | -49.52 | -51.4383 | -53.3565 | -55.2747 | -57.1929 | -59.1112 | -61.0294 | -62.9476 | -64.8658 | -66.7841 | -68.7023 | -70.6205 | -72.5387 | -74.457 | -76.3752 | -78.2934 | -80.2116 | -82.1298 | -84.0481 | -85.9663 | -87.8845 | -89.8027 | -91.721 | -93.6392 | -95.5574 | -97.4756 | -99.3939 | -101.3121 | -103.2303 | -105.1485 | -107.0667 | -108.985 | -110.9032 | -112.8214 | -114.7396 | -116.6579 | -118.5761 | -120.4943 | -122.4125 | -124.3308 | -126.249 | -128.1672 | -130.0854 | -132.0046 | -133.9319 | -135.8592
10.4766 | RBP route, 2029/30 floor | 0.4475 | -49.15% | 68.7099 |  |  | 25 | 10.4766 | 40.5976 | 39.053 | 37.5008 | 35.9487 | 34.3966 | 32.8319 | 31.2643 | 29.6898 | 28.0726 | 26.4546 | 24.8184 | 23.179 | 21.5396 | 19.8883 | 18.2291 | 16.5699 | 14.9003 | 13.2228 | 11.5453 | 9.8562 | 8.1596 | 6.459 | 4.742 | 3.0251 | 1.2998 | -0.43242 | -2.1686 | -3.9149 | -5.6633 | -7.4227 | -9.1841 | -10.9556 | -12.7594 | -14.6358 | -16.5122 | -18.3885 | -19.7853 | -20.8199 | -22.728 | -24.6389 | -26.5498 | -28.4607 | -30.3716 | -32.2825 | -34.1934 | -36.1042 | -38.0151 | -39.926 | -41.8369 | -43.7478 | -45.6587 | -47.5696 | -49.4805 | -51.3914 | -53.3023 | -55.2132 | -57.1241 | -59.035 | -60.9459 | -62.8567 | -64.7676 | -66.6785 | -68.5894 | -70.5003 | -72.4112 | -74.3221 | -76.233 | -78.1439 | -80.0548 | -81.9657 | -83.8766 | -85.7875 | -87.6984 | -89.6093 | -91.5201 | -93.431 | -95.3419 | -97.2528 | -99.1637 | -101.0746 | -102.9898 | -104.9093 | -106.8292 | -108.7498 | -110.6704 | -112.5919 | -114.5135 | -116.4353 | -118.3581 | -120.2809 | -122.2037 | -124.1265 | -126.0498 | -127.9737 | -129.8977 | -131.8217 | -133.7468 | -135.672 | -137.5972 | -139.5236 | -141.4501 | -143.3766 | -145.304 | -147.2318 | -149.1596 | -151.0875 | -153.0153 | -154.9431 | -156.8723 | -158.8015 | -160.7307
6.0983 | RBP route, 2029/30 cap | 0.339 | -61.48% | 52.0501 |  |  | 14 | 6.0983 | 22.9613 | 21.3996 | 19.8068 | 18.1936 | 16.5632 | 14.9328 | 13.2876 | 11.6372 | 9.9784 | 8.3096 | 6.6359 | 4.9486 | 3.2521 | 1.5436 | -0.17156 | -1.8955 | -3.63 | -5.3704 | -7.1217 | -8.8815 | -10.6793 | -12.5485 | -14.4178 | -15.6412 | -17.2486 | -19.1487 | -21.0505 | -22.9524 | -24.8542 | -26.756 | -28.6579 | -30.5597 | -32.4616 | -34.3634 | -36.2652 | -38.1671 | -40.0689 | -41.9708 | -43.8726 | -45.7744 | -47.6763 | -49.5781 | -51.48 | -53.3818 | -55.2836 | -57.1855 | -59.0873 | -60.9892 | -62.891 | -64.7928 | -66.6947 | -68.5965 | -70.4984 | -72.4002 | -74.302 | -76.2039 | -78.1124 | -80.0226 | -81.9337 | -83.8451 | -85.7572 | -87.6696 | -89.5829 | -91.4962 | -93.4095 | -95.3234 | -97.2378 | -99.1523 | -101.0679 | -102.9837 | -104.9006 | -106.8177 | -108.7358 | -110.6542 | -112.5727 | -114.4911 | -116.4102 | -118.33 | -120.2499 | -122.1698 | -124.0897 | -126.0095 | -127.9294 | -129.8493 | -131.7691 | -133.689 | -135.6089 | -137.5287 | -139.4486 | -141.3685 | -143.2884 | -145.2082 | -147.1281 | -149.048 | -150.9678 | -152.8877 | -154.8076 | -156.7275 | -158.6473 | -160.5672 | -162.4871 | -164.4069 | -166.3268 | -168.2467 | -170.1665 | -172.0864 | -174.0063 | -175.9262 | -177.846 | -179.7659 | -181.6858

## Customer
CUSTOMER-SIDE BENCHMARKS
Item | Value | Unit | Source
1. Customer's extra cost through RBP
RBP maximum average procurement cost | 555 | $/MW-day UCAP
Customer's capacity share per kW of load (FPR 2029/30) | 0.9232 | MW UCAP per MW
Auction price: 2029/30 cap (base) | 337.83 | $/MW-day
Auction price: 2029/30 floor | 181.91 | $/MW-day
Auction price: zero (bound) | 0 | $/MW-day
RBP charge at the 2029/30 cap | 6.0983 | $/kW-month of load
RBP charge at the 2029/30 floor | 10.4766 | $/kW-month of load
RBP charge if the auction price were zero | 15.5848 | $/kW-month of load
Minimum battery fee | 27.6535 | $/kW-month
Fee ÷ RBP charge at zero auction price | 1.7744 | x
Fee ÷ RBP charge at the 2029/30 cap | 4.5346 | x
2. Price per accredited megawatt
Accredited capacity, first year | 45 | MW UCAP
Fee per accredited MW-day | 1010.172 | $/MW-day UCAP
Fee + capacity revenue per accredited MW-day | 1348.002 | $/MW-day UCAP
3. IRAS credit and dispatch record
IRAS credit rate (non-PAI rate) | 1592.5558 | $/MWh
Rent per MWh of load | 142.3234 | $/MWh
Dispatch hours in record (1 Jan 2017 – 21 Sep 2026) | 102.6667 | hours
Dispatch days since 1 Jan 2025 | 13 | days
Dispatch hours since 1 Jan 2025 | 82.1667 | hours
Dispatch hours per year since 1 Jan 2025 | 47.7888 | hours/year
4. On-site gas: capital per accredited kW
Gas peaking capital cost, low | 1100 | $/kW | Lazard LCOE+ (Jul 2026).
Gas peaking capital cost, high | 1650 | $/kW | Lazard LCOE+ (Jul 2026).
Gas combustion turbine rating, dual fuel, 2029/30 | 76% | % | PJM ELCC class ratings, 2029/30 BRA.
Gas combustion turbine rating, 2029/30 | 59% | % | PJM ELCC class ratings, 2029/30 BRA.
Gas capital per accredited kW, low | 1447.3684 | $/kW UCAP
Gas capital per accredited kW, high | 2796.6102 | $/kW UCAP
Battery capital per accredited kW | 3002.5673 | $/kW UCAP
5. Scale of the need
Dominion data-center billing demand, 2025 | 4.2 | GW | Dominion data-center forecast (16 Sep 2025).
Dominion data-center billing demand, 2030 | 7 | GW | Dominion data-center forecast (16 Sep 2025).
New capacity that growth needs to leave the IRAS tier | 2.585 | GW UCAP